## ModvFresh
Calculation of performances of DHW ModvFresh pump units
Project data
Max temperature of storage tank | 60 | [ °C ]
Max water temperature at which the heat source can load the storage tank uniformly.
5
Inlet cold water temperature | 15 | [ °C ] | 10
Cold water temperature from the mains. |  |  | 15
Required DHW temperature | 40 | [ °C ]
Hot water temperature to user.
Required flow rate | 35 | [ l/min ]
Constant flow rate to user.
Buffer tank capacity | 300 | [ l ]
Volume of water contained in the buffer tank.
Output of the heat pump | 20 | [ kW ]
Nominal thermic power at working temperature.
For this parameter, please follow the instructions on the sheet "Example diagram reading".
Minimum water temperature in the buffer tank | 55 | [ °C ]
Report the temperature reading on the performance diagram of the specific unit, cross-referencing the 'Required flow rate' value with the 'Required temperature' curve.
Calculated performance data |  |  |  | 1 L acqua = 1 Kg massa
Overall output | 61.0458 | [ kW ] |  | Potenza erogata [W]: portata di massa [kg/s] * ΔT in erogazione [°C] * cal.specifico [J/kg°C]
Total power supplied by ModvFresh unit. |  |  |  | Esempio: | 15/60*(45-10)*4.186= 36.627,5 W
Energia utilizzabile | 6.279 | [ MJ ] |  | Energia [MJ]: massa [kg] * ΔT consumata [°C] * cal.specifico [J/g°C]
L'energia garantita dal salto di temperatura nell'accumulo. |  |  |  | Esempio: | 250*(60-52,2)*4.186=8.162.700 J
Duration of the service | 2.5496 | [ min ] |  | T erogazione [s]: energia [J] / potenza erogata [W]
Duration of the service at required flow rate and temperature. |  |  |  | Esempio: | (8.162.700 / 6.628) = 1231,6 s = 20,52 min | Se pot.gen > pot.erogata è "illimitato"
Overall draw-off | 89.2356 | [ l ] |  | Spillamento [L]: Portata [L/min] * Tempo di erogazione [min]
Overall volume of supplied hot water. |  |  |  | Esempio: | 15*20,52 = 307,8 | Se pot.gen > pot.erogata è "illimitato"
Time for restarting | 5.2325 | [ min ] |  | T ripristino [s]: energia [J] / potenza generatore [W]
Requested time to go from min to max buffer tank temperature. |  |  |  | Esempio: | 8.162.700 / 30.000 = 272 s = 4,5 min | Se pot.gen > pot.erogata è "0"
bonetti rubinetterie valduggia s.r.l.
Loc. Molino Rastelli, 2 l IT-13018 Valduggia (VC) l Tel. +39 0163 48062 l Fax +39 0163 48188
http://www.brv.it l e-mail: info@brv.it l ISO 9001:2015 Cert. No. 0853/8

## Example diagram reading
Minimum buffer tank temperature: how to derive it from diagrams
Example diagram, only valid for the model ModvFresh 2 - 70 kW with cold water inlet temperature of 10°C
Flow rate [ L/min ] | Inlet cold water temp.: 10°C
Min. requested buffer tank temp. [ °C ]
In the example shown in the above diagram, a DHW flow of 15 L/min at a temperature of 45°C is required. Crossing the desired DHW temperature curve, it follows that the supply from the buffer storage tank must be almost 52.2°C. This is the value that must be entered into the "Minimum water temperature in the buffer tank" cell of the calculation sheet.
The entire range of performances diagrams, for each specific ModvFresh model, is available on the web site www.brv.it by downloading the instructions of the individual groups (menù Products / ModvlvS / Fresh domestic hot water / ModvFresh DHW pump units).
bonetti rubinetterie valduggia s.r.l.
Loc. Molino Rastelli, 2 l IT-13018 Valduggia (VC) l Tel. +39 0163 48062 l Fax +39 0163 48188
http://www.brv.it l e-mail: info@brv.it l ISO 9001:2015 Cert. No. 0853/8